## analysis
three-phase current formula |  |  |  |  | Conductor Type | Size (kcmil) | AC Resistance (ohms/1000 ft) | Ampacity (A) | Parallel Runs Needed | Voltage Drop (%) | Cost per Foot | Key Features
[5 empty] | AAC (Overhead) | 477 | 0.032 | 705 | 15 | 16.7% | 5.5 | Lightweight, low-cost
|  |  | Answer (amps) | 10459.244 | AAC (Overhead) | 1590 | 0.009 | 1830 | 6 | 4.7% | 15.8 | Minimal voltage drop
[5 empty] | AAAC (Overhead) | 795 | 0.018 | 1120 | 10 | 9.4% | 8.2 | Corrosion-resistant
key |  |  |  |  | AAAC (Overhead) | 1590 | 0.008 | 2200 | 5 | 4.2% | 16.5 | High ampacity
variable | value |  |  |  | ACSR (Overhead) | 795 | 0.018 | 1120 | 10 | 9.4% | 8.5 | High strength
I (current: amps) | 10459.244 |  |  |  | ACSR (Overhead) | 1590 | 0.008 | 2200 | 5 | 4.2% | 17 | Steel core for heavy spans
P (real power: watts) | 200000000 |  |  |  | ACAR (Overhead) | 795 | 0.018 | 1120 | 10 | 9.4% | 9 | Balanced strength/ampacity
V (volts) | 13800 |  |  |  | ACAR (Overhead) | 1590 | 0.008 | 2200 | 5 | 4.2% | 17.5 | Alloy-reinforced
pf (power factor: unitless, 0-1) 0.8 is typical planning factor | 0.8 |  |  |  | HTLS (Overhead) | 795 | 0.016 | 1430 | 8 | 7.9% | 12 | Low sag at high temps
[5 empty] | HTLS (Overhead) | 1590 | 0.007 | 2500 | 4 | 3.6% | 22 | Carbon-fiber core
[5 empty] | Covered MVCC (Overhead) | 500 | 0.028 | 880 | 12 | 13.2% | 14 | Storm resilience
voltage drop formula |  |  |  |  | Covered MVCC (Overhead) | 1590 | 0.01 | 1950 | 6 | 4.5% | 24 | Insulated for urban areas
[5 empty] | XLPE (Underground) | 500 | 0.028 | 880 | 12 | 13.2% | 18 | Fire-resistant, armored
|  |  | Answer (volts) | 652.1739 | XLPE (Underground) | 1000 | 0.014 | 1300 | 8 | 6.5% | 26 | High-capacity underground
key |  | Entergy mandates a Vdrop of < 5% |  | 4.726% | XLPE (Underground) | 1590 | 0.009 | 1830 | 6 | 4.7% | 32 | Low-loss underground
variable | value |  |  |  | ACCR (Overhead) | 795 | 0.015 | 1600 | 7 | 6.8% | 25 | Composite core, ultra-high temp
Vdrop (voltage drop: volts) | 652.1739 |  |  |  | Silicone-Coated | 500 | 0.03 | 800 | 13 | 14% | 20 | High-temp industrial use
I (current: amps) | 10459.244
R (conductor resistance per foot: ohms/ft) | 0.009
L line length (feet) | 4000 |  |  |  | Input Parameters
[5 empty] | Power (MW) | 120
[5 empty] | Voltage (kV) | 13.8
power loss formula |  |  |  |  | Power Factor | 0.8
[5 empty] | Conductor Ampacity (A) | 1590
|  |  | Answer (watts) | 11814744.8015
key |  |  | (MW) | 11.8147 | Calculations
variable | value |  |  |  | Total Current (A) | 4016.3497
Ploss | 11814744.8015 |  |  |  | #of wires per phase | 3
I | 10459.244
R | 0.009
L | 4000
I
I=𝑃/(√3∗𝑉∗𝑝𝑓)
Vdrop
Vdrop=√3∗𝐼∗𝑅∗𝐿/1000
𝑃𝑙𝑜𝑠𝑠=3∗𝐼^2∗𝑅∗𝐿

## cost estimate
Project Details |  |  |  |  | Input Parameters |  | Underground Installation Parameters
Voltage | 13.8kV |  |  |  | Power (MW) | 120 | Project Distance (feet) | 1200
Load | 120 MW at 0.8 power factor |  |  |  | Voltage (kV) | 13.8 | Crew Daily Production Rate (feet/day) | 300
Distance | 1200 |  |  |  | Power Factor | 0.8 | Hourly Crew Cost ($) | 452.5
Conductor | 1,590 kcmil AAC |  |  |  | Conductor Ampacity (A) | 1590
total # of wires | 12 | [5 empty] | Labor Calculations
[5 empty] | Calculations |  | Hours Required | 32
[5 empty] | Total Current (A) | 6275.5464 | Total Labor Cost ($) | 14480
Summary | Overhead | Underground |  |  | # of wires per phase | 4
Total Cost | #VALUE! | 649084.8
OVERHEAD
Item | Unit | Quantity | Unit Cost | Total Cost
Conductor | feet | 72000 |  | 0
Installation Labor | hours | 56 | 390 | 21840
Poles | each | 20 | 750 | 15000
Hardware | lump sum | 1 | [Estimate] | #VALUE!
Contingency | percentage | 30% | [=SUM(E2:E5)] | #VALUE!
UNDERGROUND
Item | Unit | Quantity | Unit Cost | Total Cost
Conductor (XLPE) | feet | 14400 | 32 | 460800
Trenching | feet | 1200 | 10 | 12000
Conduit | feet | 1200 | 5 | 6000
backfill | feet | 1200 | 5 | 6000
Installation Labor | hours | 32 | 453 | 14496
Contingency | percentage | 30% | 499296 | 149788.8